## Slide 1
AC-WLS Power System State Estimation with PMU Integration
EE574 Real-Time Power System Monitoring — Semester Project
M. Aytunç Evlice
14
Buses
27
States
72
Measurements
8/8
Cases Passed
INTRODUCTION
State estimation is the core algorithm of every Energy Management System (EMS). It fuses noisy SCADA and PMU measurements into a consistent estimate of the power system operating point (bus voltages and angles), enabling real-time monitoring and control.
This project implements a full AC-WLS state estimator from scratch:
Newton-based WLS iterative solver
Analytical Jacobian (all measurement types)
Transformer π-model (off-nominal tap ratios)
PMU phasor measurement integration
Numerical observability analysis (SVD rank)
Normalized-residual bad data detection
NETWORK
IEEE 14-bus test network (1961 AEP system)
14 buses, 17 branches, 3 transformers
5 generator/slack buses, 9 load buses
Tap ratios: 6→9 (0.978), 6→10 (0.969), 4→12 (0.932)
State vector: x = [θ₂…θ₁₄, V₁…V₁₄] → 27 states
SCADA: σV = 0.005 pu, σPQ = 0.01 pu
PMU: σ = 0.0001 pu (100× more accurate than SCADA)
METHODOLOGY
State Vector
x = [θ₂ … θN, V₁ … VN] (2N−1 states, θ₁ = 0)
WLS Objective
J(x) = (z − h(x))ᵀ W (z − h(x))
W = diag(1/σᵢ²)
Newton Normal Equations (per iteration)
(HᵀWH) Δx = Hᵀ W (z − h(x))
H = dh/dx is the analytical Jacobian (all measurement types).
Convergence
Backtracking line search: step α is halved until J decreases, preventing divergence. Warm start from load-flow solution → converges in 2–3 iterations.
Observability Check
rank(H) = n_states ⟺ system is observable
Computed via SVD at flat start. PMUs at buses {2,5,9,10,12,14} restore full observability: rank 19→27, adding 45 redundant degrees of freedom.
Bad Data Detection (Normalized Residual Test)
r̄ᵢ = rᵢ / √Ωᵢᵢ
Ω = R − H(HᵀWH)⁻¹Hᵀ
Flag if |r̄ᵢ| > 3.0
Under clean conditions r̄ᵢ ~ N(0,1). Values exceeding 3.0 (3σ) indicate gross errors. The measurement with the largest |r̄ᵢ| is removed; the estimator re-runs without it.
RESULTS — THREE SCENARIOS
Scenario 1 — Original SCADA (Unobservable)
19 measurements from measure.dat (sections 1–6)
Jacobian rank: 19/27 (deficit 8 — not observable!)
Unobservable buses: 9, 10, 12, 14
WLS objective J = 25,101 (model–data mismatch)
Normalized residuals |r̄| > 10,000 — estimation unreliable
Scenario 2 — Synthetic SCADA + PMU (Clean)
72 measurements (58 SCADA + 14 PMU at buses {2,5,9,10,12,14})
Jacobian rank: 27/27 ✓ (+45 redundant degrees of freedom)
Converges in 2 iterations
RMSE voltage = 0.00055 pu | RMSE angle = 0.016°
WLS J = 42.4 ≈ degrees of freedom ✓
0 measurements flagged as bad data ✓
Scenario 3 — Bad Data Injected & Detected
+0.5 pu gross error injected into Pflow(1→3)
WLS J rises to 2,236 (clear alarm)
Largest residual: Pflow(1→3), |r̄| = 44.9 → correctly identified ✓
After removal: RMSE voltage = 0.00054 pu
State fully recovered to Scenario 2 accuracy ✓
Summary
Scenario | Meas | Rank | J_WLS | BD
Sc1: Original SCADA | 19 | 19/27 | 25,101 | N/A
Sc2: SCADA + PMU (clean) | 72 | 27/27 | 42.4 | —
Sc3: Bad data injected | 72 | 27/27 | 2,236 | YES ✓
MULTI-NETWORK VALIDATION
The estimator was validated on 8 networks from 3 to 40 buses using synthetically generated test cases. All 8/8 cases passed all four checks.
Network | Buses | States | RMSE_V (pu) | BD
3-BUS | 3 | 5 | 0.00023 | YES
5-BUS | 5 | 9 | 0.00021 | YES
IEEE-14 | 14 | 27 | 0.00087 | YES
RAND-4 | 4 | 7 | 0.00062 | YES
RAND-7 | 7 | 13 | 0.00059 | YES
RAND-10 | 10 | 19 | 0.00134 | YES
RAND-20 | 20 | 39 | 0.00067 | YES
RAND-40 | 40 | 79 | 0.00072 | YES
CONCLUSIONS
AC-WLS estimator built from scratch with analytical Jacobian and transformer π-model
PMU placement at 6 buses restores full observability (rank 19→27, +45 dof)
Normalized residual test correctly identifies injected errors (|r̄| = 44.9 vs threshold 3.0)
Estimator is robust across 3–40 bus topologies (8/8 PASS)
WLS J ≈ degrees of freedom confirms statistical consistency of clean estimates
REFERENCES
A. Monticelli, State Estimation in Electric Power Systems, Kluwer, 1999
A.J. Wood & B.F. Wollenberg, Power Generation Operation and Control, Wiley, 2013
IEEE CDF format: IEEE Trans. PAS, Vol. PAS-92, No. 6, 1973
EE574 | Real-Time Power System Monitoring | AC-WLS State Estimator | M. Aytunç Evlice
github.com/aytuncevlice/EE574_Project